# Additional Experiments Required for Q1 Journal Submission

Paper: Graph-Aware Safe Volt-VAR Control for PV-Rich Distribution Feeders

Purpose: This document lists the additional experiments needed to strengthen the paper from a proof-of-concept study into a rigorous, reproducible Q1 journal submission. The current manuscript validates the method mainly on a simplified single-phase IEEE-13-inspired feeder with three controllable inverter buses; therefore, the revision must expand validation, add fair baselines, and demonstrate robustness, safety, scalability, and practical feasibility.

# 1. Baseline Comparison Experiments

## Experiment 1.1: Standard Volt-VAR Droop Control

Purpose: Show that the proposed graph-aware safe controller performs better than conventional autonomous Volt-VAR droop control.

| Controller | Description |
| --- | --- |
| Standard Volt-VAR droop | Local voltage-based inverter droop control. |
| Proposed controller | Graph/neighbour-aware controller with stability-oriented safety filter. |

Report: voltage profiles, maximum voltage violation, recovery time, reactive-power effort, and number of saturation events.

## Experiment 1.2: Local Proportional Controller

Controller equation: u_i(t) = -k_i(v_i(t) - v_ref).

Purpose: Show the benefit of adding graph/neighbour information beyond simple local feedback.

| Controller | Local feedback | Neighbour information | Safety filter |
| --- | --- | --- | --- |
| Local proportional | Yes | No | No or limited |
| Proposed | Yes | Yes | Yes |

## Experiment 1.3: Local Safe Controller Without Graph Term

Implementation: Use g_i(t) = e_i(t) instead of the full graph potential with the neighbour-coupling term.

Purpose: Isolate the contribution of the graph/neighbour-aware term. This is one of the most important experiments because the paper claims that one-hop neighbour information improves voltage regulation.

## Experiment 1.4: Centralized OPF or Volt-VAR Optimization Baseline

Purpose: Compare the proposed lightweight decentralized method against a stronger centralized optimization benchmark.

| Controller | Expected advantage | Expected limitation |
| --- | --- | --- |
| Centralized OPF | Strong voltage regulation | Higher computation and communication burden |
| Proposed controller | Lightweight and decentralized | May be less globally optimal |

Report: voltage regulation performance, computation time per control step, communication requirement, and control effort.

## Experiment 1.5: Distributed Reactive-Power Feedback Baseline

Purpose: Implement a known distributed reactive-power feedback method from the literature to show that the proposed method is competitive with established distributed voltage-control approaches, not only simple droop control.

# 2. Ablation Studies

Goal: Prove that each component of the proposed method contributes to performance.

| Experiment | Required action and purpose |
| --- | --- |
| 2.1 Without neighbour coupling term | Set rho = 0. This removes neighbour information and tests whether the graph/neighbour term improves recovery and voltage regulation. |
| 2.2 Different neighbour coupling strengths | Test rho = 0, 0.1, 0.3, 0.5, 0.7, and 1.0. Report recovery time, max voltage violation, reactive-power effort, and stability index. |
| 2.3 Without safety gain scaling | Set alpha = 1 or remove conservative scaling. Test whether gain scaling prevents aggressive or unstable response. |
| 2.4 Without ramp-rate constraint | Remove ¦u_i(t)-u_i(t-1)¦ <= Delta u_max. Report command smoothness, oscillation, voltage recovery, and inverter stress. |
| 2.5 Without saturation constraint | Remove or relax inverter command limits. Show whether unfiltered commands exceed practical inverter capability. |
| 2.6 One-hop versus two-hop neighbour information | Compare local only, one-hop, and two-hop neighbour information to justify the selected communication structure. |

# 3. Test-Feeder Expansion Experiments

Why needed: The current validation uses a simplified single-phase IEEE-13-inspired radial feeder. For Q1 quality, the paper needs larger and more realistic feeder validation.

| Experiment | Required action and purpose |
| --- | --- |
| 3.1 Full IEEE 13-bus three-phase unbalanced feeder | Show performance beyond the simplified single-phase model. Report phase-wise voltage profiles, voltage unbalance, phase-specific reactive-power commands, recovery time per phase, and violation duration per phase. |
| 3.2 IEEE 34-bus feeder | Demonstrate scalability on a longer radial feeder. Report weak/end-bus performance, inverter-placement effect, computation time, and communication burden. |
| 3.3 IEEE 123-bus feeder | Demonstrate large-feeder scalability. Report all-bus voltage regulation, far-end node performance, runtime per step, neighbour-message count, and comparison with droop/local safe baselines. |
| 3.4 Different inverter placement scenarios | Test near-substation, mid-feeder, end-feeder, random placement, and voltage-sensitivity-based placement. Show robustness to DER location. |

# 4. PV Penetration and Disturbance Experiments

Why needed: The paper targets PV-rich feeders, so the experiments must show performance under different PV penetration levels and disturbance patterns.

| Scenario | PV penetration |
| --- | --- |
| Low PV | 20% |
| Medium PV | 50% |
| High PV | 80% |
| Very high PV | 100% or above peak load |

For PV penetration experiments, report: maximum overvoltage, violation duration, recovery time, reactive-power effort, and saturation frequency.

| Experiment | Purpose and implementation |
| --- | --- |
| 4.1 Different PV penetration levels | Test 20%, 50%, 80%, and 100% or above peak load. |
| 4.2 Rapid cloud transient scenario | Create sudden PV drops/rises, such as 100% to 40% or 30% to 90% within a few seconds, with repeated cloud-passing events. |
| 4.3 Extreme midday overvoltage scenario | Simulate high PV generation with low load demand to test overvoltage mitigation. |
| 4.4 Evening ramp scenario | Simulate decreasing PV generation with increasing residential load to test undervoltage recovery. |
| 4.5 Random stochastic PV and load profiles | Run at least 30-50 random scenarios using different seeds. Report mean ± standard deviation, boxplots, confidence intervals, and worst-case performance. |

# 5. Communication and Measurement Robustness Experiments

Why needed: Because the proposed method uses one-hop neighbour voltage information, the paper must test imperfect communication and measurement conditions.

| Experiment | Settings | Purpose |
| --- | --- | --- |
| 5.1 Communication delay | 0 ms, 100 ms, 500 ms, 1 s, 2 s | Test stability and performance when neighbour data are delayed. |
| 5.2 Packet loss / missing neighbour information | 5%, 10%, 20%, 40% packet loss | Test unreliable communication. Use last available value or local-only fallback when data are missing. |
| 5.3 Measurement noise | Gaussian noise with std. 0.001, 0.003, 0.005, 0.01 p.u. | Test sensitivity to noisy voltage measurements. |

# 6. Safety and Stability Experiments

Why needed: The paper claims the method is safe and stability-oriented. This must be demonstrated experimentally, not only stated.

| Experiment | Required action and purpose |
| --- | --- |
| 6.1 Stability index over time | Plot Delta F over time for droop, local safe, graph-aware without safety filter, and full proposed method. |
| 6.2 Control command boundedness | Verify u_min <= u_i(t) <= u_max and ¦u_i(t)-u_i(t-1)¦ <= Delta u_max. Report maximum/minimum command values, command-limit violations, and ramp-rate violations. Ramp-rate violation count should be zero. |
| 6.3 Aggressive gain stress test | Increase feedback gain gradually: 0.5k, 1k, 2k, 5k, 10k. Compare with and without the safety filter. |
| 6.4 Inverter saturation stress test | Test inverter capacity at 100%, 75%, 50%, and 25% of normal capacity. Evaluate effectiveness under limited reactive-power capacity. |

# 7. Computational and Real-Time Feasibility Experiments

Why needed: The paper claims that the proposed controller avoids centralized OPF and is suitable for real-time deployment. This must be supported by runtime and communication results.

| Experiment | Required action and purpose |
| --- | --- |
| 7.1 Computation time per control step | Measure mean, maximum, and standard deviation of runtime per step for droop, local safe, proposed graph-aware safe, and centralized OPF. Report scalability with feeder size. |
| 7.2 Communication burden | Report information exchanged per control step: local droop uses local voltage only; proposed one-hop uses local + neighbour voltages; centralized OPF requires feeder-wide data. |

# 8. Topology and Reconfiguration Experiments

Why needed: The manuscript discusses topology and reconfiguration issues in the Introduction, so at least one experiment should test topology change or DER unavailability.

| Experiment | Required action and purpose |
| --- | --- |
| 8.1 Line switching / topology change | Simulate a feeder topology change during operation. Compare fixed neighbour graph, updated neighbour graph, and local-only fallback. |
| 8.2 Fault or temporary disconnection scenario | Simulate temporary disconnection of one inverter or feeder section. Report voltage violation, recovery time, performance degradation, and fallback behaviour. |

# Minimum Experiment Set if Time Is Limited

1. Standard Volt-VAR droop baseline

2. Local safe controller baseline

3. Graph-aware controller without safety filter

4. Full proposed controller

5. Ablation with rho = 0

6. Sensitivity study for rho

7. Sensitivity study for alpha

8. PV penetration levels: 20%, 50%, 80%, and 100%

9. At least 30 random PV/load scenarios

10. Full IEEE 13-bus three-phase unbalanced feeder

11. One larger feeder: IEEE 34-bus or IEEE 123-bus

12. Communication delay test

13. Measurement noise test

14. Computation time comparison

15. Command boundedness and ramp-rate violation check

# Suggested Final Results Section Structure

| Section | Content |
| --- | --- |
| 5.1 Test systems and scenario design | IEEE 13, IEEE 34/123, PV/load settings. |
| 5.2 Baseline comparison | Droop, local safe, graph-only, proposed, and OPF. |
| 5.3 Dynamic voltage response under PV/load disturbances | Voltage and reactive-power plots. |
| 5.4 Ablation study | Effect of neighbour term and safety filter. |
| 5.5 Robustness under PV penetration and stochastic scenarios | Multiple PV/load cases. |
| 5.6 Communication delay and measurement noise analysis | Practical deployment robustness. |
| 5.7 Stability and safety analysis | Bounded commands, ramp-rate compliance, and stability index. |
| 5.8 Computational efficiency and scalability | Runtime and communication burden. |

The paper should not only show that the proposed method works on one small feeder. It must show that the method is better than standard baselines, robust across different PV/load conditions, safe under inverter constraints, scalable to larger feeders, and practical under communication delay/noise. These additional experiments will make the paper much more suitable for a Q1 journal.